## Cover
Green Real Estate
Gas shortage situation ¦ Checklist for Site Managers to Increase Energy Efficiency in Buildings
Intended for internal use
2022-12-01
Disclaimer: - This document does not claim to be fully comprehensive. - It is intended as a support tool for facility managers to implement short-term energy saving measures at the customer's site. We suggest that the facility manager goes through the list and implements the steps and measures that are relevant to their customer and add further measures that are relevant for their customer. - Any measures that have a noticeable impact on building occupants need to be discussed with the customer. - The document is not subject to regular updates.
Karen Rück
Green Real Estate Product Manager
karen.rueck @apleona.com
+49 152 56174344
(Central Cotact)

## Energy Optimization
Checklist for Energy Optimization in Buildings
1 | Heating, Air Conditioning, Ventilation | (1) Measure reviewed | (2.1) Measure implemented | (2.2) Not implented - support needed | (2.3) Not implemented - not meaningful | Comment
1.1 | Take a look at the night reduction of the HVAC systems and suggest to your customer - depending on the use of the building - a situation-related adjustment (e.g. by starting the system later in the morning and switching it off earlier in the evening). --> At best, a reduction of at least 2h is possible. Alternatively, only a part of the building area could be heated or cooled separately at extraordinary times. | ⃝ | ⃝ | ⃝ | ⃝
1.2 | Analyse at the operating hours or setback operation of the HVAC systems on weekends and holidays. Suggest to your customer - depending on the use of the building - a situation-related reduced operating time or extended setback operation. --> For example, only part of the area could be heated or cooled separately, but not the entire building. | ⃝ | ⃝ | ⃝ | ⃝
1.3 | Check the current setting of the room temperature. Then suggest to your customer to decrease it (in winter) or to increase it (in summer). --> In winter: A target value would be 19° Celsius (the Workplace Ordinance(ASR 3.5) prescribes a room temperature of 20° Celsius for light sedentary work. However, the Ordinance on Securing the Energy Supply through Measures Effective in the Short Term (EnSikuMaV) allosws a temporary reduction of one degree Celsius). --> In summer: A target value would be 25° Celsius (according to the Workplace Ordinance (ASR 3.5) , the air temperature in workrooms should not exceed 26° Celsius). | ⃝ | ⃝ | ⃝ | ⃝
1.4 | Discuss with your customer the reduction of the heating temperature (in winter) or the reduction or even switching off of the cooling (in summer) in areas that are not used for the permanent stay of people, such as staircases, hallways, entrance halls and lobbies and implement if possible. | ⃝ | ⃝ | ⃝ | ⃝
1.5 | Check the flow and return temperatures of your heating system and optimize it to the minimum (just high enough to achieve the desired room temperature) and/or optimize the heating curve in case of major errors in the setting. Please make sure that the flow and return temperatures have an appropriate spread. | ⃝ | ⃝ | ⃝ | ⃝
1.6 | Review the switching times of your door/or air curtain, if possible reduce it in consultation with your customer. | ⃝ | ⃝ | ⃝ | ⃝
1.7 | Check the humidity control of the air conditioning system and whether the dehumidification function can be deactivated. | ⃝ | ⃝ | ⃝ | ⃝
1.8 | Check the possibility of a connection to an existing district heating network. | ⃝ | ⃝ | ⃝ | ⃝
1.9 | Verify if pumps in static heating mode can be shut down during the summer months. | ⃝ | ⃝ | ⃝ | ⃝
1.10 | During the summer: Make sure buildings are shaded and blinds are down on the sunny side. | ⃝ | ⃝ | ⃝ | ⃝
2 | Water | (1) Measure reviewed | (2.1) Measure implemented | (2.2) Not implented - support needed | (2.3) Not implemented - not meaningful | Comment
2.1 | Discuss with your customer to turn off the hot water heating or to reduce the temperature to the minimum hygienic level (to prevent legionella formation; when water is used for hand washing). | ⃝ | ⃝ | ⃝ | ⃝
2.2 | Check if storage temperature of heated water can be reduced in view of the current situation. | ⃝ | ⃝ | ⃝ | ⃝
2.3 | Discuss with your customer the possible installation of water-saving faucets or flow restrictors or so-called aerators. | ⃝ | ⃝ | ⃝ | ⃝
Additional measures to save water
2.4 | Are there ornamental fountains in front of the building? | ⃝
2.4.1 | If yes: Coordinate a shutdown with your customer. | ⃝ | ⃝ | ⃝ | ⃝
2.5 | Are outdoor facilities (e.g. lawn areas) watered? | ⃝ | ⃝ | ⃝ | ⃝
2.5.1 | If yes: Coordinate with your customer if irrigation can be reduced. | ⃝ | ⃝ | ⃝ | ⃝
3 | Electricity | (1) Measure reviewed | (2.1) Measure implemented | (2.2) Not implented - support needed | (2.3) Not implemented - not meaningful | Comment
3.1 | Review your client's interior night and object lighting and suggest to your client to turn them off (for example, between 10 p.m. and 6 a.m.). | ⃝ | ⃝ | ⃝ | ⃝
3.2 | Check if there is a possibility to optimize the stairwell and hallway lighting, e.g., using motion detectors and shorter run times of timers. | ⃝ | ⃝ | ⃝ | ⃝
3.3 | Check if there is a possibility to optimize the lighting of outdoor areas, e.g., through the use of motion detectors and shorter run time of timers. | ⃝ | ⃝ | ⃝ | ⃝
3.4 | Implement the shutdown of illuminated or light-emitting advertising equipment at night from 10 p.m. to 4 p.m., unless required for public safety reasons or by law or administrative order. This is also mandated by the regulation to secure energy supply through short-term effective measures of the federal government (EnSimiMaV). | ⃝ | ⃝ | ⃝ | ⃝
3.5 | Check the illumination levels for possible reductions. | ⃝ | ⃝ | ⃝ | ⃝
3.6 | Review the replacement of conventional lighting techniques to LED and implement it accordingly. (Note: T5 and T8 luminaires will be phased out soon!) | ⃝ | ⃝ | ⃝ | ⃝
4 | Consumption & Space Management | (1) Measure reviewed | (2.1) Measure implemented | (2.2) Not implented - support needed | (2.3) Not implemented - not meaningful | Comment
4.1 | Do you have access to your customer's energy consumption data? | ⃝
4.1.1 | If yes: Check the energy consumption of the buildings for irregularities and peaks and, if possible, derive simple and more specific measures. (For example, are there noticeably high night loads?). | ⃝ | ⃝ | ⃝ | ⃝
4.1.2 | If so: Analyze the building consumption and identify the locations with the lowest and highest energy consumption and lowest and highest usage. | ⃝ | ⃝ | ⃝ | ⃝
4.1.3 | If no: Approach your client and suggest that they conduct a Rapid Energy Review. (The Rapid Energy Review is carried out by the CoC Energy & Sustainability by inspecting the building and building technology on site and based on specific data and subsequently proposing short-term energy savings.) | ⃝ | ⃝ | ⃝ | ⃝
4.2 | Discuss with your customer which areas, buildings or entire sites can be closed (if available; under the consideration of energy consumption, employee usage, and effects on technical equipment). | ⃝
4.2.1 | If yes: Ensure heating/cooling is significantly reduced in enclosed areas/buildings/locations. | ⃝ | ⃝ | ⃝ | ⃝
4.2.2 | If yes: Offer to assist your client with any necessary moves. | ⃝ | ⃝ | ⃝ | ⃝
4.2.3 | If yes: Offer to manage a potential space vacancy appropriately for your client. | ⃝ | ⃝ | ⃝ | ⃝
5 | Internal Customer Measures & Crisis Management | (1) Measure reviewed | (2.1) Measure implemented | (2.2) Not implented - support needed | (2.3) Not implemented - not meaningful | Comment
5.1 | Ask your customer if they already have appropriate employee awareness communications and if not provide these documents. | ⃝ | ⃝ | ⃝ | ⃝
5.2 | Please find out who is the central contact for crisis management at the customer so that you can respond quickly should there be widespread sanctions including rationing of gas. | ⃝ | ⃝ | ⃝ | ⃝
5.2.1 | Additionally ask whether the company already has a gas emergency plan in place and what measures, if any, are already being implemented. Feel free to offer your assistance with appropriate measures. | ⃝ | ⃝ | ⃝ | ⃝
5.3 | Already consider the consequences of a potential gas shortages for your client:
5.3.1 | Which systems are critically affected or could be damaged in the event of shutdowns and must, for example, be maintained separately or need special measures that must be taken to shut these down? | ⃝ | ⃝ | ⃝ | ⃝
5.3.2 | What is the cost and what would need to be done to turn the technical equipment back on? | ⃝ | ⃝ | ⃝ | ⃝
5.3.3 | As an extension to Measure 4.2, which employees can work from the home office (similar to Corona) and which spaces/buildings/locations can be closed? | ⃝ | ⃝ | ⃝ | ⃝